## lighting calculation
Floor | Calculated Space | Calculation (L×W) | Area (m2) | Lux Level (E) | Lumen Output per Luminaire (Φ) | Z | UF | MF | Raw Calculated (Nraw​) | Selected (Ndesign​)
Ground Floor | Bed Room | (4.50×3.525)+(1.8×2.225) | 19.87 | 100 | 1100 | 1 | 0.6 | 0.8 | 3.76 | 4
Ground Floor | Dining and Living Room | 5.668×2.9 | 16.44 | 200 | 2100 | 1 | 0.6 | 0.8 | 2.45 | 3
Ground Floor | Pantry | 2.025×2.975 | 6.02 | 250 | 1100 | 1 | 0.6 | 0.8 | 1.71 | 2
Ground Floor | Toilet | 2.225×1.700 | 3.78 | 150 | 1100 | 1 | 0.6 | 0.8 | 1.07 | 2
Ground Floor | Driver's Room | 2.667×1.800 | 4.8 | 200 | 1100 | 1 | 0.6 | 0.8 | 0.91 | 1
Ground Floor | Care Taker Room | 2.50×1.725 | 4.31 | 150 | 1100 | 1 | 0.6 | 0.8 | 0.82 | 1
Ground Floor | Showers Room | 1.5×0.9 | 1.35 | 150 | 1100 | 1 | 0.6 | 0.8 | 0.38 | 1
Ground Floor | Toilet Drivers | 1.5×0.9 | 1.35 | 150 | 1100 | 1 | 0.6 | 0.8 | 0.38 | 1
Ground Floor | Pump Room | 4.914×2.0+1.8×0.3 | 10.37 | 150 | 4000 | 1 | 0.6 | 0.8 | 0.81 | 1
Ground Floor | Elect. Meters & Panels | 1.300×2.400 | 3.12 | 200 | 2500 | 1 | 0.6 | 0.8 | 0.39 | 1
Ground Floor | Garbage Room | 1.300×2.400 | 3.12 | 100 | 1350 | 1 | 0.6 | 0.8 | 0.48 | 1
Ground Floor | GF Lobby & Stairs | (3.926×3.537)+(2.400×6.337) | 29.1 | 150 | 2200 | 1 | 0.6 | 0.8 | 4.13 | 4
Ground Floor | Parking Area | (2.40×4.80)×3 | 34.56 | 100 | 4000 | 1 | 0.6 | 0.8 | 1.8 | 2
3rd Floor Left | Master Bedroom | 3.900×3.600 | 14.04 | 100 | 1100 | 1 | 0.6 | 0.8 | 2.66 | 4
3rd Floor Left | Bed Room | 3.900×3.300 | 12.87 | 100 | 1100 | 1 | 0.6 | 0.8 | 2.44 | 4
3rd Floor Left | Sitting Areas | 3.80×6.337 | 24.08 | 150 | 2100 | 1 | 0.6 | 0.8 | 3.58 | 4
3rd Floor Left | Dining Areas | 3.80×2.025 | 7.7 | 150 | 1100 | 1 | 0.6 | 0.8 | 2.19 | 2
3rd Floor Left | Pantries | 3.80×2.400 | 9.12 | 150 | 1100 | 1 | 0.6 | 0.8 | 2.59 | 4
3rd Floor Left | Kitchen Yards | 3.80×1.500 | 5.7 | 100 | 1350 | 1 | 0.6 | 0.8 | 0.88 | 1
3rd Floor Left | Master Toilets | 2.70×1.50 | 4.05 | 150 | 1100 | 1 | 0.6 | 0.8 | 1.15 | 2
3rd Floor Left | Master Balcony | 3.900×1.500 | 5.85 | 100 | 1350 | 1 | 0.6 | 0.8 | 0.9 | 1
3rd Floor Left | Balcony | 3.90×1.00 | 3.9 | 100 | 1350 | 1 | 0.6 | 0.8 | 0.6 | 1
3rd Floor Right | Master Bedroom 1(DW5) | (3.900×3.285)+(1.475×2.700) | 16.79 | 100 | 1100 | 1 | 0.6 | 0.8 | 3.18 | 4
3rd Floor Right | Master Bed Room 2(DW4) | 3.348×3.000 | 10.04 | 100 | 1100 | 1 | 0.6 | 0.8 | 1.9 | 2
3rd Floor Right | Master Bed Room 3(DW3) | 3.382×3.833 | 12.96 | 100 | 1100 | 1 | 0.6 | 0.8 | 2.46 | 4
3rd Floor Right | Master Toilets 1(DW5) | 2.700×1.400 | 3.78 | 150 | 1100 | 1 | 0.6 | 0.8 | 1.07 | 2
3rd Floor Right | Master Toilets 2(DW4) | 2.700×1.500 | 4.05 | 150 | 1100 | 1 | 0.6 | 0.8 | 1.15 | 2
3rd Floor Right | Master Toilets 3(DW2) | 2.700×1.400 | 3.78 | 150 | 1100 | 1 | 0.6 | 0.8 | 1.07 | 2
3rd Floor Right | Sitting Areas | 4.005×6.337 | 25.38 | 150 | 2100 | 1 | 0.6 | 0.8 | 3.78 | 4
3rd Floor Right | Dining Areas | 3.631×2.025 | 7.35 | 150 | 1100 | 1 | 0.6 | 0.8 | 2.09 | 2
3rd Floor Right | Pantries | 4.200×2.400 | 10.08 | 150 | 1100 | 1 | 0.6 | 0.8 | 2.86 | 4
3rd Floor Right | Kitchen Yards | 4.200×1.500 | 6.3 | 100 | 1350 | 1 | 0.6 | 0.8 | 0.97 | 1
3rd Floor Right | Master Balcony 1(DW5) | 3.900×1.500 | 5.85 | 100 | 1350 | 1 | 0.6 | 0.8 | 0.9 | 1
3rd Floor Right | Master Balcony 2(DW4) | 3.000×1.500 | 4.5 | 100 | 1350 | 1 | 0.6 | 0.8 | 0.69 | 1
3rd Floor Right | Master Balcony 3(DW2) | 3.833×1.00 | 3.83 | 100 | 1350 | 1 | 0.6 | 0.8 | 0.59 | 1
3rd Floor Right | Typ. Lobby & Stairs | 6.337×2.400 | 15.21 | 150 | 2200 | 1 | 0.6 | 0.8 | 2.16 | 2
Roof Top | Generator Room | 2.50×3.300 | 8.25 | 150 | 4000 | 1 | 0.6 | 0.8 | 0.64 | 2
Roof Top | gym | 4.10×3.338 | 13.69 | 300 | 3600 | 1 | 0.6 | 0.8 | 2.38 | 4
Roof Top | Changing Room & Toilet | 1.50×0.900 | 1.35 | 150 | 1100 | 1 | 0.6 | 0.8 | 0.38 | 1
Roof Top | Bar / BBQ Counter | 3.113×2.039 | 6.35 | 150 | 1350 | 1 | 0.6 | 0.8 | 1.47 | 2
Roof Top | Roof Lobby & Stairs | 2.400×6.337 | 15.21 | 150 | 2200 | 1 | 0.6 | 0.8 | 2.16 | 2
Roof Top | Open Terrace | 7.325×6.337 | 46.42 | 50 | 2400 | 1 | 0.6 | 0.8 | 2.01 | 2

## Lighting
Floor | Space | Type of Light | Power Per Lamp | Selected No. of Luminaries
(W)
Ground floor | Bed Room | CoreLine Slim Downlight 10s | 11 | 4
| Dining and Living Room | CoreLine Slim Downlight 20s | 21 | 4
| Pantry | CoreLine Slim Downlight 20s | 21 | 3
| Toilet | CoreLine Downlight | 9.5 | 2
| Driver's Room | CoreLine Slim Downlight | 11 | 2
| Care Taker Room | CoreLine Slim Downlight | 11 | 1
| Showers Room | CoreLine Downlight | 9.5 | 1
| Driver’s Toilet | CoreLine Downlight | 9.5 | 1
| Pump Room | CoreLine Waterproof | 30 | 1
| Elect. Meters & Panels | CoreLine Batten | 18 | 1
| Garbage Room | CoreLine Wall-Mounted | 12 | 1
| GF Lobby & Stairs |  | 21 | 4
CoreLine Slim Downlight
| Parking Area | CoreLine Waterproof | 30 | 2
Roof floor | Generator Room | CoreLine Waterproof | 30 | 2
| gym | CoreLine Panel | 28.5 | 4
| Changing Room & Toilet |  | 9.5 | 1
CoreLine Downlight
| Bar / BBQ Counter | CoreLine Wall-Mounted | 12 | 2
| Roof Lobby & Stairs | CoreLine Downlight | 19 | 2
| Open Terrace | Ledinaire Floodlight |  | 6
20
| corridor | SmartBright Direct Panel (G2) | 28 | 2
| pool deck | Philips Wall-Mounted LED (Outdoor) | 15 | 10
| pool | Philips Ledinaire Underwater/Spot | 20 | 6
1 to 3rd floor | Master Bedroom L | CoreLine Slim Downlight LED10S | 11 | 4
| Bed Room L | CoreLine Slim Downlight LED10S | 11 | 3
| Sitting Areas | CoreLine Slim Downlight LED20S | 21 | 4
| Dining Areas | CoreLine Slim Downlight LED10S | 11 | 2
| Pantries | CoreLine Slim Downlight LED10S | 11 | 4
| Kitchen Yards | (CoreLine Wall-Mounted | 12 | 1
| Master Toilets | CoreLine Downlight IP54 P16 | 9.5 | 2
| Master Balcony | CoreLine Wall-Mounted | 12 | 1
| Balcony | CoreLine Wall-Mounted | 12 | 1
| Master Bedroom R | CoreLine Slim Downlight LED10S | 11 | 4
| Bed Room 1R | CoreLine Slim Downlight LED10S | 11 | 2
| Bed Room 2R |  | 11 | 4
CoreLine Slim Downlight LED10S
| Master Toilets | CoreLine Downlight IP54 P16 | 9.5 | 2
| Toilets 1 | CoreLine Downlight IP54 P16 | 9.5 | 2
| Toilets 2 | CoreLine Downlight IP54 P16 | 9.5 | 2
| Sitting Areas R | CoreLine Slim Downlight LED20S | 21 | 4
| Dining Areas | CoreLine Slim Downlight LED10S | 11 | 2
| Pantries | CoreLine Slim Downlight LED10S | 11 | 5
| Kitchen Yards | CoreLine Wall-Mounted | 12 | 1
| Master Balcony 1(DW5) | CoreLine Wall-Mounted | 12 | 1
| Balcony 1 | CoreLine Wall-Mounted | 12 | 1
| Balcony 2 | CoreLine Wall-Mounted | 12 | 1
| Typ. Lobby & Stairs | CoreLine Downlight C P16 | 19 | 2

## ground floor
Area | Space | Load | No. of Units | KW per Load | Power Factor | KVA | Diversity Factor | Utilization Factor | Total KVA with Factors
Apartment | Bedroom | AC | 1 | 1.7 | 0.85 | 2 | 0.8 | 0.9 | 1.44
|  | Sockets | 4 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.306
| Dining Room | AC | 1 | 1.7 | 0.9 | 2 | 0.8 | 0.9 | 1.44
|  | Sockets | 5 |  | 0.9 | 0.18 | 0.5 | 0.9 | 0.405
| Kitchen | Exhaust Fan | 1 | 0.75 | 0.9 | 0.83 | 1 | 1 | 0.83
|  | Sockets | 5 |  | 0.95 | 0.18 | 0.4 | 1 | 0.36
| toilet | Sockets | 2 |  | 0.85 | 0.18 | 0.5 | 1 | 0.18
| All | Lighting |  | 0.21 | 0.9 | 0.23333 | 0.66 | 0.85 | 0.1309
Common | Lobby | AC | 1 | 1.7 | 0.85 | 2 | 0.8 | 0.9 | 1.44
| Pump room | Water Pumps | 1 | 1.5 | 0.9 | 1.67 | 0.75 | 0.9 | 1.1273
|  | Sockets | 4 |  | 0.9 | 0.18 | 0.5 | 1 | 0.36
| Elect Meter Panel | Sockets | 2 |  | 0.9 | 0.18 | 0.5 | 1 | 0.18
| Drivers room | Sockets | 2 |  | 0.9 | 0.36 | 0.5 | 1 | 0.36
| Care Takers Room | sockets | 2 |  | 0.9 | 0.18 | 0.5 | 1 | 0.18
| all lighting in common | lighting |  | 0.196 | 0.9 | 0.22 | 0.66 | 0.85 | 0.12342
| Parking Area and drive way | Sockets | 6 |  | 0.9 | 0.18 | 0.5 | 1 | 0.54
|  | Lighting | 4+6 | 0.24 | 0.9 | 0.26667 | 0.66 | 0.85 | 0.1496
[7 empty] | Total KVA |  | 9.5522

## Roof floor
Space | Load | No. of Units | KW per Load | Power Factor | KVA | Diversity Factor | Utilization Factor | Total KVA with Factors
Bar / BBQ Counter | Kitchen Equipment | 1 | 5 | 0.9 | 5.5556 | 0.8 | 1 | 4.4444
| Sockets | 4 |  | 0.85 | 0.5 | 0.5 | 0.85 | 0.85 | Generator Room
Pool and pool deck | Pool Equipment | 1 | 3 | 0.9 | 3.3333 | 0.9 | 1 | 3 | Changing Room & Toilet
| Sockets | 4 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.306 | Bar / BBQ Counter
Generator Room | Sockets | 3 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.2295
Changing Room & Toilet | Sockets | 2 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.153
Open terrance | sockets | 6 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.459
elevator | motor | 1 | 6 | 0.9 | 6.6667 | 0.7 | 0.9 | 4.2
roof floor | lighting | 29 | 0.571 | 0.9 | 0.63444 | 0.66 | 0.85 | 0.35592
[6 empty] | Total KVA |  | 13.9979
20% expansion

## Left aprtment
Area | Space | Load | No. of Units | KW per Load | Power Factor | KVA | Diversity Factor | Utilization Factor | Total KVA with Factors | Design Current(A)
Apartment | master Bedroom | AC | 1 | 1.7 | 0.85 | 2 | 0.8 | 0.9 | 1.44 | 13.86
|  | socket | 4 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.306
| Bedroom | AC | 1 | 1.7 | 0.85 | 2 | 0.8 | 0.9 | 1.44
|  | Sockets | 4 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.306 | 2.08
| Dining Room and sitting room | AC | 1 | 1.7 | 0.85 | 2 | 0.8 | 0.9 | 1.44
|  | Sockets | 6 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.459
| Pantry & kitchen yard | Exhaust Fan | 1 | 0.75 | 0.9 | 0.83333 | 0.9 | 1 | 0.75
|  | Sockets | 6 |  | 0.85 | 0.6 | 0.5 | 0.85 | 1.53
| Balcony | sockets | 3 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.2295
| Toilets | sockets | 2 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.153
| all | lighting | 22 | 0.282 | 0.9 | 0.31333 | 0.66 | 0.85 | 0.17578
Common | Lobby & Stair | sockets | 2 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.153
|  | Lighting | 2 | 0.038 | 0.9 | 0.042222 | 0.66 | 0.85 | 0.023687
[7 empty] | Total KVA |  | 8.406
Area | Circuit | Space | Load | No. of Units | KW per Load | Power Factor | KVA | Diversity Factor | Utilization Factor | Total KVA with Factors | Design Current(A) | Total Design Current | MCB Rating | Main Breaker (MCCB)
Left Appartment | C1 | Master bedroom + Balcony + Bathroom | AC | 1 | 1.7 | 0.85 | 2 | 0.8 | 0.9 | 1.44 | 4.4194 | 4.4194 | 10/1p | 16/3p
| C2 |  | Socket Outlet | 4 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.306 | 2.3478 | 2.3478 | 16/1p
| C3 |  | Lighting | 5 | 0.011 | 0.9 | 0.024444 | 0.66 | 0.85 | 0.068567 | 0.35774 | 0.35774 | 6/1p
|  | Toilet | Lighting | 1 | 0.011 | 0.9 | 0.0125 | 0.66 | 0.85 | 0.01 | 0.024
| C4 | Bedroom 1 + Balcony | AC | 1 | 1.2 | 0.85 | 1.4118 | 0.8 | 0.9 | 4 | 4.4194 | 4.4194 | 10/1p
| C5 |  | Socket Outlet | 4 | 0.18 | 0.85 | 0.18 | 0.5 | 0.85 | 0.54 | 2.3478 | 2.3478 | 16/1p
| C6 |  | Lighting | 4 | 0.022 | 0.9 | 0.024444 | 0.66 | 0.85 | 0.08712 | 0.37878 | 0.37878 | 6/1p
|  | Toilet | Lighting | 2 | 0.011 | 0.9 | 0.0125 | 0.66 | 0.85 | 0.01 | 0.024
| C7 |  | AC | 1 | 1.2 | 0.85 | 1.4118 | 0.8 | 0.9 | 1.44 | 4.4194 | 4.4194 | 10/1p
| C8 | Dinning & Sitting+balcony | Socket Outlet | 6 | 0.18 | 0.85 | 0.21176 | 0.5 | 0.85 | 0.54 | 0.4 | 2.3478 | 16/1p
| C9 |  | Lighting | 4 | 0.0285 | 0.9 | 0.031667 | 0.66 | 0.85 | 0.10659 | 0.46343 | 0.46343 | 6/1p
| C10 | Kitchen | Socket Outlet | 6 | 0.45 | 0.85 | 0.52941 | 0.5 | 0.85 | 0.9 | 3.913 | 3.913 | 16/1p
| C11 |  | Lighting | 5 | 0.0355 | 0.9 | 0.039444 | 0.66 | 0.85 | 0.066385 | 0.28863 | 0.28863 | 6/1p
| C12 |  | Exhaust | 1 | 0.75 | 0.85 | 0.88235 | 0.9 | 1 | 0.79412 | 3.4527 | 3.4527 | 6/1p
| Demand (KVA/Current) | [8 empty] | 6.7059 | 9.6794
| With 20% Future expansion | [8 empty] | 8.0471 | 11.6153

## right aparment
Area | Space | Load | No. of Units | KW per Load | Power Factor | KVA | Diversity Factor | Utilization Factor | Total KVA with Factors
Apartment | master Bedroom | AC | 1 | 1.7 | 0.85 | 2 | 0.8 | 0.9 | 1.44
|  | socket | 4 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.306
| Bedroom 1 | AC | 1 | 1.7 | 0.85 | 2 | 0.8 | 0.9 | 1.44
|  | sockets | 4 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.306
| Bedroom 2 | AC | 1 | 1.7 | 0.85 | 2 | 0.8 | 0.9 | 1.44
|  | Sockets | 4 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.306
| Dining Room and sitting room | Sockets | 6 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.459
| Pantry & kitchen yard | Exhaust Fan | 1 | 0.75 | 0.9 | 0.83333 | 0.9 | 1 | 0.75
|  | Sockets | 6 |  | 0.85 | 0.6 | 0.5 | 0.85 | 1.53
| Balcony | sockets | 4 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.306
| Toilets | sockets | 3 |  | 0.85 | 0.18 | 0.5 | 0.85 | 0.2295
| all | lighting | 22 | 0.376 | 0.9 | 0.41778 | 0.66 | 0.85 | 0.23437
[7 empty] | Total KVA |  | 8.7469
20% expansion

## Sheet2
Area | Circuit | Space | Load | No. of Units | KW per Load | Power Factor | KVA | Diversity Factor | Utilization Factor | Total KVA with Factors | Design Current(A) | Total Design Current | MCB Rating | Main Breaker (MCCB)
Left Appartment | C1 | Master bedroom + Balcony + Bathroom | AC | 1 | 1.2 | 0.85 | 1.4118 | 0.8 | 0.9 | 1.0165 | 4.4194 | 4.4194 | 10/1p | 16/3p
| C2 |  | Socket Outlet | 6 | 0.18 | 0.85 | 0.21176 | 0.5 | 0.85 | 0.54 | 2.3478 | 2.3478 | 16/1p
| C3 |  | Lighting | 6 | 0.022 | 0.9 | 0.024444 | 0.66 | 0.85 | 0.08228 | 0.35774 | 0.35774 | 6/1p
| C4 | Bedroom 1 + Balcony + Bathroom | AC | 1 | 1.2 | 0.85 | 1.4118 | 0.8 | 0.9 | 1.0165 | 4.4194 | 4.4194 | 10/1p
| C5 |  | Socket Outlet | 6 | 0.18 | 0.85 | 0.21176 | 0.5 | 0.85 | 0.54 | 2.3478 | 2.3478 | 16/1p
| C6 |  | Lighting | 6 | 0.022 | 0.85 | 0.025882 | 0.66 | 0.85 | 0.08712 | 0.37878 | 0.37878 | 6/1p
| C7 |  | AC | 1 | 1.2 | 0.85 | 1.4118 | 0.8 | 0.9 | 1.0165 | 4.4194 | 4.4194 | 10/1p
| C8 | Dinning & Sitting+balcony | Socket Outlet | 6 | 0.18 | 0.85 | 0.21176 | 0.5 | 0.85 | 0.54 | 2.3478 | 2.3478 | 16/1p
| C9 |  | Lighting | 6 | 0.0285 | 0.9 | 0.031667 | 0.66 | 0.85 | 0.10659 | 0.46343 | 0.46343 | 6/1p
| C10 | Kitchen | Socket Outlet | 4 | 0.45 | 0.85 | 0.52941 | 0.5 | 0.85 | 0.9 | 3.913 | 3.913 | 16/1p
| C11 |  | Lighting | 3 | 0.0355 | 0.9 | 0.039444 | 0.66 | 0.85 | 0.066385 | 0.28863 | 0.28863 | 6/1p
| C12 |  | Exhaust | 1 | 0.75 | 0.85 | 0.88235 | 0.9 | 1 | 0.79412 | 3.4527 | 3.4527 | 6/1p
| Demand (KVA/Current) | [8 empty] | 6.7059 | 9.6794
| With 20% Future expansion | [8 empty] | 8.0471 | 11.6153
Right Appartment | C1 | Master bedroom + Balcony + Bathroom | AC | 1 | 1.2 | 0.85 | 1.4118 | 0.8 | 0.9 | 1.0165 | 4.4194 |  | 10/1p | 20/3p
| C2 |  | Socket Outlet | 6 | 0.16 | 0.85 | 0.18824 | 0.5 | 0.85 | 0.48 | 2.087 |  | 16/1p
| C3 |  | Lighting | 6 | 0.022 | 0.9 | 0.024444 | 0.66 | 0.85 | 0.08228 | 0.35774 |  | 6/1p
| C4 | Bedroom 1 + Balcony + Bathroom | AC | 1 | 1.2 | 0.85 | 1.4118 | 0.8 | 0.9 | 1.0165 | 4.4194 |  | 10/1p
| C5 |  | Socket Outlet | 6 | 0.16 | 0.85 | 0.18824 | 0.5 | 0.85 | 0.48 | 2.087 |  | 16/1p
| C6 |  | Lighting | 6 | 0.022 | 0.9 | 0.024444 | 0.66 | 0.85 | 0.08228 | 0.35774 |  | 6/1p
| C8 | Bedroom 1 + Balcony + Bathroom | Socket Outlet | 6 | 0.16 | 0.85 | 0.18824 | 0.5 | 0.85 | 0.48 | 2.087 |  | 16/1p
| C9 |  | Lighting | 6 | 0.022 | 0.9 | 0.024444 | 0.66 | 0.85 | 0.08228 | 0.35774 |  | 6/1p
| C10 | Dinning & Sitting | AC | 1 | 1.2 | 0.85 | 1.4118 | 0.8 | 0.9 | 1.0165 | 4.4194 |  | 10/1p
| C11 |  | Socket Outlet | 6 | 0.18 | 0.85 | 0.21176 | 0.5 | 0.85 | 0.54 | 2.3478 |  | 16/1p
| C12 |  | Lighting | 6 | 0.0285 | 0.9 | 0.031667 | 0.66 | 0.85 | 0.10659 | 0.46343 |  | 6/1p
| C13 | Kitchen | Socket Outlet | 4 | 0.45 | 0.85 | 0.52941 | 0.5 | 0.85 | 0.9 | 3.913 |  | 16/1p
| C14 |  | Lighting | 3 | 0.0355 | 0.9 | 0.039444 | 0.66 | 0.85 | 0.066385 | 0.28863 |  | 6/1p
| C15 |  | Exhaust | 1 | 0.75 | 0.85 | 0.88235 | 0.9 | 1 | 0.79412 | 3.4527 |  | 6/1p
| Demand (KVA/Current) | [8 empty] | 7.1433 | 10.3108
| With 20% Future expansion | [8 empty] | 8.572 | 12.373
Other |  | Lobby + Staircase | Lighting | 2 | 0.0285 | 0.9 | 0.031667 | 0.66 | 0.85 | 0.03553 | 0.15448 |  | 6/1p